Extruded Tapered Insulation Systems

New Roof Construction (or Total Tear Off)

Below Membrane Specification

Section 07220 Roof Insulation Materials

NOTES:  Tapered Thermapink or FOAMULAR below membrane insulation systems include mechanically attached, fully adhered, or ballasted single ply or modified bitumen or BUR.

[Bracketed boldface] information must be edited to suit the use of Tapered Thermapink or FOAMULAR in a particular insulation below membrane system.  Boldfaced underlined information is explanatory for review as needed.  Generally such information need not be included in the specification.

PART 1 – GENERAL

1.01 Description of Work

- Furnish and install Tapered [Thermapink, FOAMULAR] in strict accordance with Drawings and Specifications and per Owens Corning's published literature.

1.02 Quality Assurance

- Roofing system must be applied by a roofing contractor authorized by the membrane manufacturer.

- Install tapered roof insulation in accordance with the manufacturer's approved shop drawings.

- Each tapered panel shall be labeled with a code letter to identify its slope and to identify its proper position on the roof.  Each panel shall also be marked with an arrow to identify direction of slope.

- Each tapered insulation board and each flat fill board must be labeled with manufacturer's name, product brand name, ASTM material specification reference, and identification of the third party inspection agency used for building code qualification. UL and FM certification documents and Material Safety Data Sheets are available from Owens Corning on request.

- [Upon completion of ballasted roof construction the owner's representative must verify that installation is in accordance with design specifications such as adequate ballast gradation, rate of coverage and areas covered.]

1.03 Product Delivery, Storage and Handling

- Deliver insulation materials in original unopened packaging.

- Store insulation materials in dry area and protect from water and direct sunlight.  Damaged insulation materials shall not be used and shall be replaced.  In the event the Thermapink or FOAMULAR insulation becomes wet, the insulation can be wiped dry and then installed without harm to the insulation or the roof system.

- Tapered [Thermapink, FOAMULAR] insulation is combustible, but contains a flame retardant additive to inhibit accidental ignition from small fire sources.  During shipping, storage, installation and use, this material should not be exposed to flame or other ignition sources.

- For proper fire protection of plastic foam in storage, consult the National Fire Protection Association (NFPA) standards or the authority having jurisdiction.

1.04 Job Conditions (Cautions and Warnings)

- Roof deck shall be free of ponded water, ice or snow.  This precaution is to discourage potential future condensation on the underside of the membrane.

- Do not expose Tapered [Thermapink, FOAMULAR] insulation to surfaces such as vent stacks, pipes or other rooftop appurtenances whose constant temperature is in excess of 165°F.  If temperature cycling conditions are anticipated near the maximum recommended use temperature, consult an Owens Corning representative for recommendations regarding system components.

- When insulation is to be exposed to sunlight for prolonged periods due to job site delays, protect the insulation with a light colored opaque covering.  Provisions should be made to prevent wind loss of insulation materials at the job site when partially open units of Tapered [Thermapink, FOAMULAR] are on hand.

- Dark membrane ballasted systems must have ballast installed immediately after installation of membrane.  This precaution is required to prevent potential damage to the insulation from excessive heat due to prolonged exposure to sunlight.

- Roofs exposed to chemical discharge require special consideration.  Consult an Owens Corning representative for recommendations regarding system components.

- [Any deteriorated decking shall be repaired or replaced.  Existing roof drains must be verified to be open and adequate to promote proper roof drainage.]

1.05 Building Code Compliance

The roof covering assembly and its individual components must comply with all applicable building code requirements.  
Only Thermapink is intended for use directly over steel roof decks with no thermal barrier, constructed in accordance with UL Roof Deck Construction #457.  FOAMULAR or Thermapink may be used over steel deck WITH thermal barrier when needed for FM Class I, or when the limits of UL construction #457 are exceeded.  Tapered systems that, by design, vary in maximum thickness, and often have greater maximum thicknesses, should be verified for compliance with UL construction #457.

Consult local building code for applicable requirements regarding the need for a thermal barrier (UL 1256/FM 4450), rooftop exterior surface spread of flame or fire penetration (ASTM E108), structural fire resistance (ASTM E119), wind uplift resistance, or other applicable requirements.

1.06 Warranty

A thermal performance warranty must be issued to the project owner upon completion of the work.  [Insulation must be warranted to retain a minimum of 90% of its published R-value for 15 years.]  [A single source full roof covering system warranty must be issued to the project owner upon completion of the work.]  Consult an Owens Corning representative for information on obtaining warranties.  Single source full system warranties are available for certain roofing systems.

PART 2 – PRODUCTS

2.01 Related Materials

- Extruded Polystyrene Insulation

  - Physical Properties:
Tapered Materials:  Tapered [Thermapink, FOAMULAR] closed-cell foam panels with continuous as-extruded skin on the face and back surfaces, conforming to the minimum physical requirements of ASTM C-578, Type IV.

Fill Materials:  [Thermapink 18, 25, 40] [FOAMULAR 250, 400, 600] closed-cell foam panels with continuous as-extruded skin on the face and back surfaces, conforming to the minimum physical requirements of ASTM C-578, [Type X, IV, VI, VII].  See the Physical Properties section of this manual for Thermapink or FOAMULAR physical properties and association with ASTM C578 type designations.  No further specification of physical properties is required if a standard ASTM C578 type designation is given.  However if the specifier chooses to elaborate, it should be verified that the specified properties align with the chosen ASTM type category.  Contact an Owens Corning representative for more information about the current ASTM C578 material standard.

  - Panel size:  Provide rigid Tapered [Thermapink, FOAMULAR] insulation panels [slope/foot x width x length].

Provide rigid [Thermapink, FOAMULAR] insulation panels for use as fill material [thickness x width x length].  See the Product Availability section of this manual for product sizes.

- [Insulation Fasteners and Stress Plates]:  if needed in mechanically attached system

Furnished by membrane manufacturer if applicable.  Fasteners and stress plates shall be FM approved.  Fastener head shall be designed to inhibit damage to the membrane.  Minimum 3" diameter or square insulation stress plates shall provide for countersunk fastener heads.

- [Thermal Barrier]:  Not needed over concrete or wood decks.  Not needed when Thermapink is used over steel deck in accordance with UL Roof Deck Construction #457.  Needed only when FOAMULAR is specified over steel deck, or the limits of #457 are exceeded, or FM Class I steel deck assembly is needed.

Thermal barrier material must be as specified in the building code or  classified by assembly testing in accordance with UL 1256 or FM 4450  and shall be placed as prescribed in the assembly listing over steel decks.  Approved thermal barriers include ½” (minimum thickness) gypsum board and ½” (minimum thickness) rigid perlite board.  See the UL Classified Steel Roof Decks and FM Class I Steel Decks charts in this manual for complete information.  Consult appropriate listing documents such as the “FMRC Approval Guide” or “UL Roofing Materials and Systems Directory” for alternative thermal barrier materials and complete assembly details.

- [Overlayment]:  Needed with dark mechanically attached, or any color fully adhered, or chemically incompatible membranes.

[Wood fiber overlayment board shall conform to ASTM C208; minimum ½” thick.]  [Flexible glass fiber, nonwoven, non-flammable, corrosion and mildew resistant or other suitable separator (overlayment) sheets shall be used under PVC membranes and other such membranes which contain plasticizing agents.  Separator sheet shall have been evaluated and approved by the membrane manufacturer for adequacy as a separator.]  In all cases the membrane manufacturer's recommendation regarding insulation overlayment shall prevail.

- Membrane and [fastening, adhesion] system:

Per membrane manufacturer’s specifications.

- [Ballast]:  If needed in loose laid, ballasted system.

[All ballast shall be [rounded water worn gravel, crushed stone, smooth concrete pavers].]  Building height, parapet height and project wind zone are major factors when specifying a minimum ballast requirement.  Design of ballasted systems should be accomplished in accordance with ANSI/SPRI RP-4, Wind Design Guide for Ballasted Single-Ply Roofing Systems.

[Gravel or crushed stone ballast shall conform to ASTM D448, size [#3, #24, #2, #1].]

[Concrete pavers must have a compressive strength equal to [___psi] or greater, maximum water absorption rate of  [__% by volume], and dimensions, not exceeding 2" x 2' x 2' ].  Paver weight must be manageable for removal and replacement purposes.  Concrete quality must be suitable for weathering conditions to which it will be subjected.

PART 3 – EXECUTION

3.01 Roof Deck Criteria

                - The deck shall be constructed to drain completely free of water within 48 hours following rainfall.

                - The dead load carrying capability of the deck must be sufficient to support code mandated live loads and dead loads incident on the roof including the entire roof covering/insulation system.

                - The roof deck shall be prepared to provide adequate support for the insulation.

3.02 Roof Deck Preparation

[Any deteriorated roof decking shall be repaired or replaced.]

A thorough inspection should be required in the case of total tear off.

[Steel Roof Decking]:  Install a thermal barrier between Tapered [Thermapink, FOAMULAR]/fill layers and the steel deck in accordance with construction drawings.

Tapered/fill Thermapink layers may be installed directly over steel roof deck in accordance with the details of UL Roof Deck Construction #457.

Tapered/fill FOAMULAR layers in a steel deck application must be underlaid with a thermal barrier as specified by the building code, or, classified by assembly in accordance with UL 1256 or FM 4450.  Thermal barriers may be loose-laid or secured to the deck by mechanical fastening depending on design or code requirements.

[Structural Concrete (precast, poured-in-place, gypsum, or lightweight insulating)]:  The surface must be clean, smooth, free of fins, sharp edges, loose and foreign materials, oil, grease, and fresh roofing cement.  Repair any deck joints or cracks, any deck to wall junctions, and any other deck to penetration gaps, which are greater than ¼”.

[Composite (Tectum, etc.)]:  Install deck and secure in accordance with deck manufacturer’s recommendations.  The deck must be properly secured with all mechanical fasteners flush with the surface of the deck.  The deck must be of sufficient thickness and character to develop adequate fastener holding power.  Verify requirements with the membrane manufacturer.

[Wood (plank, plywood, OSB, etc.)]:  Install deck and secure in accordance with construction drawings.  The deck must be well secured with all mechanical fasteners flush with the surface of the deck.  The deck must be of sufficient thickness to develop adequate fastener holding power.  Verify requirements with the membrane manufacturer.

3.03 Vapor Retarder

Install a vapor retarder in accordance with construction drawings.  Place the vapor retarder to insure adequate end and side joint laps.  When high relative humidities inside the building or other normal climatic conditions create a condensation point within the insulation board, it may be necessary to install a vapor retarder beneath the insulation or thermal barrier.  Although Tapered/fill layers of Thermapink and FOAMULAR have vapor retarding qualities, the need for more effective vapor retarding layers must be assessed based on the conditions present on each project.  Tapered and fill layers of Thermapink and FOAMULAR are compatible with most commonly used asphaltic and sheet film vapor retarding materials.  See the American Society of Heating, Refrigerating and Air Conditioning Engineers (ASHRAE) Handbook of Fundamentals for specific design guidelines.

3.04 Insulation

                - Total roof insulation aged thermal resistance shall be [R___], achieved in the thicknesses and number of layers as shown in the construction documents.  R-value chosen is to be specified based on the intended use of each project and design criteria of each project, and applicable energy conservation codes.  Contact an Owens Corning representative for information regarding ASHRAE 90.1 Energy Code minimum requirements for roof insulation if needed.

                - Install thicknesses of fill in accordance with shop drawings prepared by Owens Corning and approved by the roofing contractor.  Install Tapered [Thermapink, FOAMULAR] over the required base layers, following the directional arrow printed on each panel which indicates direction of slope.  Note that Tapered [Thermapink, FOAMULAR] panels also have a letter code printed on their surface which corresponds with panel layout shown on the approved shop drawings.

                - Insulation joints shall not exceed ¼” in width.  Joints wider than ¼” shall be filled with the same insulation.

                - Insulation shall be field trimmed to fit tightly around roof protrusions and terminations.

                - Apply only as much Tapered [Thermapink, FOAMULAR] and fill roof insulation as can be covered by the roofing membrane on the same day.  Apply roof insulation in parallel rows with end joints staggered.  Install side and end joints closely but do not force together.  In a two layer application, apply second layer panels parallel to the first layer but with side and end joints staggered in relation to the first layer.

                - Insulation shall be [loosely placed, secured] in accordance with membrane manufacturer’s requirements.  The insulation below the membrane is to be held in place with [ballast, compatible adhesives, mechanical fasteners in conjunction with the overlayment and/or membrane system].  [Mechanical fasteners shall be of sufficient number and adequate pattern to resist displacement of insulation by wind uplift forces.]  When adhering or exposing Tapered/fill Thermapink or FOAMULAR to hot bitumen, the bitumen must be allowed to cool to between 200°F and 250°F.

3.05 Overlayment

                - Only dry overlayment materials shall be used.  If overlayment materials become wet, allow them to fully dry before proceeding with roofing application.  Requirements for overlayment materials and thickness may vary.  Contact membrane manufacturer for their individual requirements.

                - [Rigid overlayment shall be [mechanically attached, adhered with a suitable adhesive] per manufacturer’s recommendations.]  Mechanical fastening of insulation and rigid overlayment may coincide so that fastener penetrates overlayment and Thermapink or FOAMULAR into the structural substrate the minimum distance prescribed for adequate wind uplift resistance by the fastener manufacturer.  [Loose lay flexible sheet overlayment over Tapered [Thermapink, FOAMULAR] and cover with a membrane attached per the manufacturer’s recommendations.  Edges and ends of rolls shall be lapped a minimum of 6".]

                - When cleaning agents and seam adhesives used are solvent based and capable of causing cavitation of the underlying [Thermapink, FOAMULAR] insulation, use care when preparing membrane edges for in-field seam splicing.

[3.06 Ballast]  If needed.  Before selecting this roofing system, it must be determined that the ballast system designed will not exceed the dead load limits of the structure.

- Ballasting Requirements:

  - Weight of ballast installed must be sufficient to provide protection against wind uplift pressure.  The necessary weight per square foot, gradation and application surface areas shall be determined in accordance with ANSI/SPRI RP-4, Wind Design Guide for Ballasted Single-Ply Roofing Systems.

  - Ballast gradation and quantity installed, i.e., depth must be adequate to completely cover the membrane.  Insulation thickness does not affect the amount of ballast required.

  - Protect membrane and place ballast in accordance with membrane manufacturer’s instructions.

[3.07 Fasteners]  If needed.

                - Fastener/stress plate assemblies shall be driven to tightly secure the insulation board and seat the plate but shall not be overdriven so that the Tapered [Thermapink, FOAMULAR] board is crushed beneath the plate.

                - Fasteners which are improperly installed shall be removed or corrected.  Improper installation may include overdriving such that the stress plate is concave and cuts a significant depression in the insulation; underdriving such that the fastener head is not properly seated in the stress plate and may puncture the membrane; broken or bent shanks; improper location; or insufficient length.

                - Fasteners shall be embedded in the deck per manufacturer’s recommendations to insure adequate withdrawal resistance.

                - Tapered [Thermapink, FOAMULAR] shall be secured with 4 fasteners and 3” diameter stress plates per 2’ x 8’ board.  Four fasteners, pattern C, (see FM listings for pattern description), are required when Thermapink or FOAMULAR is installed under white membranes with or without a slipsheet.  Four fasteners, 6” from each corner, are also required when Thermapink or FOAMULAR is installed under a rigid coverboard.  The coverboard and Thermapink or FOAMULAR may be fastened concurrently.  The rigid coverboard may require more than 4 fasteners to meet the recommendation of its manufacturer.